WASH Cluster

Technical Guidance on Water Quality Monitoring in NARGIS affected areas

- Introduction

Purpose: This note has been drafted to harmonize the interventions of agencies assisting GoUM in providing water supply with respect to water quality and testing of the quality of the water supplied.

GoUM Water Quality Standards (draft, 2006): in January 2007 a group of Myanmar experts representing various government agencies and augmented by some individuals agreed to a draft list of water quality standards (Report of the national workshop on water safety plans for townships: capacity building for pro-active water quality management, Department of Health, Yangon, February 2007).  A full copy of this report is available on the portal under WASH cluster.

It is proposed that for all practical purposes this guidance will be followed in water supply interventions

Situation analysis: Nargis has destroyed many water supply systems and contaminated many of the water sources available for drinking water use.  In Ayeyarwady and Yangon Divisions 24 townships had a piped water supply system. Some 3300 protected wells and 930 ponds and 250 dug wells were constructed during the period 2000-2006 (UNICEF, December 2006). To augment supplies many households collect rainwater as well.

In the aftermath of Nargis, disinfectant chlorine solution (mainly Water Guard) has been supplied to families, and bleaching powder has been channeled through health authorities and other agencies to the townships.

Sanitation is highly unsatisfactory in both townships and village tracts. Temporary settlements have been provided with adequate water and sanitary facilities. Staffs of the Environmental Sanitation Division of the Department of Health have been posted to the Township Medical Office in all affected townships.

Interventions: For the village tracts and hamlets, supplies are likely to come from ponds and from the collection of rainwater (for the next 3 months). Safe water should be assured through Water Guard (or similar), household filters or boiling. For townships, restoration of earlier existing supplies, or construction of temporary supplies has been/will be done using mobile water purification plants, using ground water and storage ponds. Safe water will be delivered when these plants are properly operated.

Longer term interventions will be considered later, in consultation with authorities and beneficiary population. Even then, current interventions should be screened against sustainability (embedding in a more durable water supply solution) and an exit strategy.

- Water Quality and its Importance

The current monsoon rains are providing sufficient water for affected population to access water for personal hygiene and laundry. Safe drinking water is however needed for direct consumption and food preparation. Drinking contaminated water may lead to disease outbreaks. Moreso, as many people are staying together in stressed water, sanitation and food conditions waterborne diseases may easily spread.

Water Quality Monitoring is done to ensure that beneficiaries are getting safe water.  The World Health Organization publishes the Guidelines for Drinking Water Quality. The 3rd edition was published in 2004.  Myanmar Water Quality Standards (draft, 2006) are proposed based on a review of the WHO Guidelines.

During emergencies we are most concerned that the water is bacteriologically safe. In other words, it should not carry any germs that can cause immediate illness, such as diarrhoea, cholera, etc. Several other parameters such as turbidity are less important, although people may not want to drink water that is brownish. Saline, salty-tasting water is no problem for a short while, except that people may not be willing to drink it and so look for other, sometimes unsafe sources.

If groundwater is used in the Ayeyarwady delta, the water may have arsenic beyond the proposed Myanmar standard. For a few weeks that may not be a problem as levels are not excessive. But when a permanent water supply is to be developed, the presence of arsenic and possibly other chemicals that have a adverse health effects should be determined and taken care of.

3. Major WQ Parameters:

There are many water quality parameters potentially of relevance such as:

- Bacteriological parameter: Thermo Tolerant Coliform (TTC), ) (also known as E.Coli or fecal coliform);

- Physical parameter: Colour, Odour, Taste, Turbidity, Temperature, PH, Conductivity, Suspended and Settleable Solids

- Chemical Parameter: Alkalinity, Acidity, Hardness, Biological Oxygen Demand (BOD), Chemical Oxygen Demand (COD), Ammonia, Nitrate and Nitrite, Total Dissolved Solids (TDS), and the ionic contents of Calcium, Magnesium, Sodium, Potassium, Iron, Chlorides, Sulphates, Carbonates, Bi carbonates, Fluorides.

In the context of the Nargis emergency, the most important water quality parameters are: E.coli., turbidity, pH, conductivity. When chlorination is used in a distribution system - pipeline, tanker truck or small bicycle water drum, free residual chlorine (FRC) should be tested as well. When free residual chlorine between 0.2 and 0.5 mg/l is maintained, testing for E.coli may not be necessary.

Additional parameters such as Arsenic, Iron and Manganese can be considered for specific geographic locations, but are not really important for the time being.

PH should preferably between 6.8 and 7.2 to reduce the amount of chlorine required. Water with turbidity over 5 NTU requires more chlorine to oxidize organic matter. See also http://wedc.lboro.ac.uk/who_Technical_notes_for_emergencies/ for further advice.

Total Dissolved Solid (TDS) or Conductivity is the measure of dissolved salts and electrolytes in water sample. The greater the salinity, the greater will be the conductivity value. People would not like to drink water that is too saline.

4. Reference Guideline for Water Quality Parameters

The following are the recommended limiting value of important water quality parameters.

| SN | Water Quality Parameters | Limiting value | Remarks |
| --- | --- | --- | --- |
|  | Thermo Tolerant Coliform (TTC) | 0 colonies in 100 ml of sample water | Very low risk, water safety is verified. It is unlikely that water will cause any significant disease in the community. |
|  |  | 1-10 colonies/ 100 ml of sample water | Low risk; water can be considered as being conditionally verified, but attempts should be made to improve quality. Water is likely to contribute to infectious disease, but will be a minor contributor compared to other routes. |
|  | Turbidity | 5 NTU | The higher the turbidity, the less will be the effectiveness of chlorine application |
|  | PH | 6.5 to 8.5 | preferably between 6.8 and 7.2 to reduce the amount of chlorine required |
|  | Total Dissolved Solid (TDS) | 100 - 1000 mg/l | More salinity means bad taste and people start rejecting it after certain point; refer to the diagram below. |
|  | Arsenic | 0.05 mg/l | Health based |
|  | Iron | 0.3 mg/l |  |
|  | Manganese | 0.3 mg/l |  |
|  | Fluoride | 1.5 mg/l | Health based |

Although TTC should preferably be 0, it would be acceptable to aim for drinking water containing less than 10 colonies per 100ml giving some consideration to practical difficulties. It assumes that people would have use of Water Guard to make their water safe at home.

The diagram below shows the limiting range of TDS for various uses of water.

Figure 1: Diagram showing optimal range of TDS for various uses

5. Frequency of Water Testing

The water quality has to be tested at least once after disinfecting the newly installed or rehabilitated water supply system. The following are the recommended water quality testing frequencies in the normal situation.

| Water Quality Parameter | Water Testing Frequency |  |  |  |
| --- | --- | --- | --- | --- |
|  | Communal Rainwater System (RWS) | Household RW System | Shallow Tube Well (STW) | Hand dug well |
| Turbidity | 3 months | 20% of RWS in a year | 20% of STW in a year | 60 days |
| PH | 3 months | 20% of RWS in a year | 20% of STW in a year | 60 days |
| Thermo-Tolerant Coliform (TTC) | 3 months | 20% of RWS in a year | 20% of STW in a year | 60 days |
| Total Dissolved Solid (TDS) |  |  | 20% of STW in a year | 60 days |

For mobile treatment plants follow the manual the comes with the treatment plant.

6. How to Measure Different Parameters?

6.1 Thermo-tolerant Coliform (TTC)

Thermotolerant Coliform (TTC) is measured applying varieties of methods: Presence/ Absence test kit and Membrane Filter methods. Presence/Absence Methods use H2S based or pathoscreen based techniques, whereas, Membrane Filter Method uses DelAgua and Wagtech kits, and ELEs.

Presence Absence Method

Steps for H2S Based Methods

- Fill the given bottle with sample water and shake well to dissolve chemicals in the bottle into the sample water.

- Wait for next 24 hours and observe the color change in the solution.

- Record the color change of the solution to black and or development of strong smell, which indicates the presence of TTC.  No color change means absence of TTC.

Membrane Filter Method

Steps for Delagua Kit

- Filter the sample water through membrane filter of standard pore size.

- Allow bacteria to grow for 18 hours in some form of growth media -Membrane Lauryl Sulphate Broth - at the standard temperature of  44 OC.

- Count the colonies of bacteria using simple lens/microscope.

Fig 4: Sample with Many colonies		 Fig 5: Sample with Zero Colonies

Wagtech kit also uses almost similar procedure. For detail steps for using Delagua or Wagtech Kit, refer to particular equipment manual.

Note: Importance of free residual chlorine in TTC presence/absence:

It is believed that the chlorine in water react with the certain enzymes which are necessary for metabolic processes of the bacteria and render them inactive. Such inactivation either causes the death or permanent inactivation of bacteria. Availability of free residual chlorine of at least 0.2 mg/l is enough to produce such effect.

6.2 Free Residual Chlorine

Check whether the free residual chlorine in sample water is more than 0.2 mg/l or not. If there is more than 0.2 mg/l and turbidity is less than 5 NTU, no need go for further steps as this indicates absence of TTC. Apply pool tester to determine free residual chlorine.

1A: Prepare pool tester, methyl red and DPD1 tablet

1B: Clean, Rinse and fill pool tester with

sample water.

1C: Add DPD1 tablet into water column labeled with DPD, crush, close lid and shake well.

Step 1D: Compare color of the solution with

Color comparator and record free

residual chlorine amount.

Note: Difference between total and free residual chlorine

There are two types of chlorine residuals in water - total chlorine residual and free chlorine residual or simply total chlorine and residual chlorine. When chlorine is added to sample water, part of it is utilized to kill the bacteria and oxidizing the organic materials there and the rest will appear as residual chlorine to act against further bacterial intrusion.

6.3 Turbidity

Turbidity is commonly measured using simple turbidity tube. It can also be measured more easily by applying digital turbidity meter. The unit of Turbidity is NTU and Zero NTU means cleanest water.

Fig 2: Turbidity Tube

Steps in using Turbidity Tube

Step 1: Rinse the turbidity tube with sample water for 2 to 3 times.

Step 2: Hold the tube vertically and pour water sample into the tube slowly in stages of few centimeters of water column at a time.

Step 3: Try to see the black cross or cycle at the bottom of the tube after each addition of water column from the top of the tube. Keep on doing this until the black cross or circle at the bottom of the tube just disappears.

Fig 3: Black circle at the bottom of turbidity tube

Step 4: Hold the tube vertically and read turbidity in NTU using the graduation on the side of the tube. The result is the value of the line nearest the water level.

6.4 Total Dissolved Solid (TDS)

Total Dissolve Solid (TDS) is measured using conductivity meter in mg/l. TDS is related to conductivity which is measured in µS/cm. The conversion factor is as:

TDS in mg/l  =  (055 – 0.9) * Conductivity in µS/cm.

Here, sample water is filled in a tube and placed inside the TDS meter. Press start button on and get TDS reading in digital screen??

Fig 4: Digital TDS/Conductivity meter

ENDS

In an emergency there is no point in measuring coliform bacteria as their sources could be many, including from sources that are not relevant to human disease transmission.