GUIDELINES ON CHLORINATION PRACTICES

May  2005

Some water sources contain disease-causing organisms which need to be removed or killed before the water is safe to drink. If carefully undertaken and monitored, disinfection is an effective means of removing such organisms. Chlorine is the most widely used disinfectant, and one which is often the most readily available.

## Chlorine demand and Chlorine residual

When chlorine is added to a water source, it purifies the water by damaging the cell structure of bacterial pollutants, thereby destroying them. The amount of chlorine needed to do this is called the chlorine demand of the water. The chlorine demand varies with the amount of impurities in the water. It is important to realize that the chlorine demand of a water source will vary as the quality of the water varies. The aim of chlorination is to satisfy the chlorine demand of the water source.

Once the demand has been satisfied, any excess chlorine above the level needed to satisfy the demand remains as a residual of chlorine (chlorine residual) in the supply. If a supply is to be adequately disinfected, therefore, there should be a chlorine residual in the supply, so that there is the capacity to cope with any subsequent bacterial contamination. The chlorine residual should generally be in the range 0.2 to 0.5 mg/l of chlorine in treated water. Any more than this and the supply may taste bad and be harmful, and people may refuse to use it. Any less, and there is no guarantee that the supply is adequately protected. An example is given in the Figure below.

All forms of chlorine are harmful to health

Avoid skin contact and do not inhale the fumes.

Chlorine should be stored in cool, dark, dry and sealed containers, and out of reach of children.

(Source: WEDC Loughborough University www.lboro.ac.uk/departments/cv/wedc/ )

## To achieve an effective chlorination, the water must be clear (turbidity < 5 NTU) and the pH should be <8.5.

On the market, there are different products that can be used for chlorination. Each of them has a different percentage of active chlorine, that is, the active ingredient.

One common product is the Sodium Hypochloride, that is in liquid form (the common household bleach), and normally  has a active chlorine percentage of 5 – 12 % .However. the most common product used in Sri Lanka is the Calcium Hypochlorite, that is in form of white powder. According to the quality, the active chlorine rate is between 35% and 75%.In this case it is also called HTH

## Jar test

From what discussed above, it is not possible to determine in advance the right quantity of chlorine to be added to a water supply, as this depend on the bacteriological content. Moreover, there are a number of different products, each of them has a different percentage of active chlorine; sometimes the label on the containers are spoiled, or get partially or totally removed during transport and storage.

To overcome those inconveniences, a procedure called “Jar Test” have been developed to ensure a correct chlorination. This procedure can be performed in the field, and if flexible enough to meet all the different situations.

### Material needed

To conduct a jar test, the following material is needed:

1 	small container of known volume (i.e. 1 liter)

4 (5) 	big containers of known volume (i.e. 10 liters)

1 	syringe 5 or 10 ml

1	measuring device for approximately 10 g (i.e. a tea spoon, or a matchbox)

1	free chlorine comparator

Note: this procedure is valid for any product, any container size, and any measuring units. In this example, it is assumed that the product used is HTH, with 70% of active chlorine. In case of  hypochlorite with 35% of chlorine, the quantities of powder to be used will be approximately doubled.

### Test

Never add the chlorination powder directly to the water to be chlorinated.

A solution (slug) of concentrate chlorine has to be prepared prior the chlorination.

- Fill all the containers with the water to be chlorinated

- Label all big (20 l) containers with

- Add 1 container (spoon) of your chlorination product to the small (1 l) container, and mix until the chlorine powder is completely dissolved

i.e. if HTH, with a 70% of active chlorine is used, to prepare 1% solution (10g of active chlorine per litre), 10 / 0.70  = 14.28g of HTH will be needed, approximately 1 spoon.

- Fill the syringe with the concentrate solution

- Add the concentrate solution to the big containers in increasing quantities:

i.e.

- 1st container:  1 ml

- 2nd container: 1.5 ml

- 3rd container : 2 ml

- 4th container 2.5 ml

- 5th container 3 ml

- Mix the containers, and wait at least 30 minutes

- Measure the residual chlorine of each container

- Choose the container that shows a residual chlorine between 0.2 and 0.5 mg/l. This is the required concentration of chlorine for the disinfection of the water

If no container has the right residual chlorine, repeat the exercise with different quantities. i.e. 2 – 4 – 8- 16 ml

In the example below, 1 spoon of HTH was added to a 1 liter container, and the containers were of 20 l capacity. The right concentration was reached adding 2 ml, it means that to chlorinate, i.e. 2000 liters of water, 200 ml of 1 spoon/liter solution has to be added, or 0.2 spoons.

| "Jar test" calculator for Chlorination |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| "Slug" Preparation |  |  |  |  |  |  |  |
| Standard measuring device ("spoon") |  | N. | 1 | in | 1 | liters |  |
| "Slug" concentration | (spoons/liter) |  | 1 |  |  |  |  |
| Jar Test |  |  |  |  |  |  |  |
| Test Jar Volume (l) | 20 |  |  |  |  |  |  |
|  |  |  | Jar 1 | Jar 2 | Jar 3 | Jar 4 | Jar 5 |
| "Slug" added | ml |  | 1 | 1.5 | 2 | 2.5 | 3 |
| Concentration | ( spoons/liter) |  | 0.00005 | 0.000075 | 0.0001 | 0.000125 | 0.00015 |
| Measured Residual Chlorine |  |  | 0 | 0.1 | 0.4 | 0.8 | 1.2 |
| (Check the Jar between 0.2 and 0.5) |  |  |  |  |  |  |  |
| Chlorination need |  |  |  |  |  |  |  |
| Volume to be chlorinated | (liters) | 2 000 |  |  |  |  |  |
| N. of spoons to be used |  |  |  |  | 0.20 |  |  |

## DPD Free Chlorine Comparator

The most common test to measure the residual chlorine levels is the DPD (diethyl paraphenylene diamine) indicator test, using a comparator. With this test, a tablet reagent is added to a sample of water, colouring it red. The strength of colour is measured against standard colours on a chart to determine the chlorine concentration. The stronger the colour, the higher the concentration of chlorine in the water. Several similar kits for analysing the chlorine residual in water are available commercially. The kits are small and portable.

Step 1

Pour the water to be tested in the comparator

Step 2

Add 1 tablet DPD No. 1

Step 3

Shake well until the tablet is completely dissolved

Step 4

Compare the color of the water against the standard colors in the kit in full light on a white background and note the result

Ideal residual should be 0.2 – 0.5 mg/l

## Wells Chlorination

From the above explanation, it is clear how the chlorination process is effective only if conducted in a very specific manner, and requires a good understanding of the procedures.

During the tsunami emergency phase large quantities of chlorine have been distributed through the affected zone, and often misused. One of the most common misuse of chlorine is the practice to chlorinate directly the water in the wells, called well chlorination.

In principle, the chlorination of water directly in the wells is not necessarily a bad idea, and has some potential advantages, i.e. if the water is than pumped to a high reservoir, difficult to reach, or a large number of different users will make use of the well independently. However, there are a number of arguments against well chlorination:

- Whenever the well is used, water is abstracted from the aquifer, and replaces the abstracted one. It means that the chlorine in the well gets more and more diluted, and the residual chlorine levels are not constant. It means that water in a chlorinated well is often over-chlorinated for a period and under-chlorinated for another period.

- The user should know how much chlorine, if any, is still in the well as a residual from the previous one, in order to be in the position to calculate correctly the right new dosage: this is virtually impossible

- If the well has lateral openings, or damages, the water table naturally flows through the well, and therefore the chlorinated water s replaced by untreated water.

- The exact volume of water to chlorinated has to be known, to avoid over or under-dosage. The estimation of the volume in the wells is often approximate.

- Chlorination is effective only with levels of turbidity lower than 5 NTU. Water in open wells is often higher than this value.

For the above mentioned reasons it is highly recommended that chlorination is conducted in a tank, or container, of known volume, after the abstraction from the well. This will permit a correct water treatment. In case of a high number of different users, household level tablets, along side with known volume containers, can be distributed, previous appropriate hygiene promotion and explanation on the correct use of the same.

## Shock chlorination of wells

Chlorination of wells on a regular base, as method to ensure the safety of the water for drinking purposes, it is not recommended. However, during the well rehabilitation exercise, or in case of algae growth, or unpleasant smells, a one-off, shock chlorination can be requested.

In a shock chlorination, the water must reach concentration of at least 200 mg/l of chlorine, for at least 2 hours. Water with this level of chlorine is not fit for human consumption, being 1,000 times higher than the level of chlorine requested in drinking water (0.2 mg/l) and must therefore be removed after the exercise. It means that the shock chlorination must be conducted before the pumping of the well.

### Recommendations for shock chlorination of wells:

WARNING

- Shock chlorination is a one-off, emergency procedure, involves large quantities of chemicals, requires extensive pumping of the well, and therefore must be conducted only in case of effective need.

- Shock chlorination is meant to disinfect the well from the products of decomposition of organic matter entered in the well as a consequence of the tsunami or after a period in which the well have been abandoned, to clear algae, worms, and other unwished dangerous items

- Shock chlorination is not a method to ensure the safety of drinking water

- The water that received a shock chlorination has a level of chlorine that exceeds 1,000 times the recommended levels for drinking water, therefore can not be consumed, and must be removed from the well before use

- Shock chlorination must be conducted by trained personnel. The beneficiaries must be informed not to drink, for any reason, the water of the well until full replacement of the water takes place.

Procedure:

- Calculate the volume of water in the well ( d/22 * 3.14 * (D-h) )

- Calculate the quantity of chlorine needed (according to the product used and the grade in free chlorine) to reach a level of chlorine of 200 mg/l (in case of HTH with a level of free chlorine of 75%, it will be 260 g/m3 of water)

- Carefully dissolve the chlorine powder in a 20 l water container and pour the concentrate solution in the well. Mix the water in the well.

- Wait for at least 2 hours (up to 24 hours)

- Slowly pump out 1/3 of the volume of the water in the well (or proceed with de-sludging with pump/compressor)

- Wait for complete recovery of the water level, than repeat pumping

- When the water in the well has been replaced, check the residual chlorine levels (see later on) in the water. If the levels exceed 0.5 mg/l of free chlorine, pump another stage.

# Calcium Hypochlorite

# Hazard Fact Sheet

## 1. Product Identification

Synonyms: Hypochlorous Acid, Calcium Salt; Losantin; Calcium Hypochloride; Chlorinated lime 
Molecular Weight: 142.98 
Chemical Formula: CaCl2O2

## 2. Composition/Information on Ingredients

Ingredient                                Percent        Hazardous

---------------------------------------   ------------   ------------

Calcium Hypochlorite                         100%          Yes

## 3. Hazards Identification

Emergency Overview 
-------------------------- 
DANGER! STRONG OXIDIZER. CONTACT WITH OTHER MATERIAL MAY CAUSE FIRE. CORROSIVE. CAUSES BURNS TO ANY AREA OF CONTACT. HARMFUL IF SWALLOWED OR INHALED. WATER REACTIVE. 

Potential Health Effects 
---------------------------------- 

Inhalation: 
Corrosive. Extremely destructive to tissues of the mucous membranes and upper respiratory tract. Symptoms may include burning sensation, coughing, wheezing, laryngitis, shortness of breath, headache, nausea and vomiting. Inhalation may be fatal as a result of spasm inflammation and edema of the larynx and bronchi, chemical pneumonitis and pulmonary edema. 
Ingestion: 
Corrosive. Swallowing can cause severe burns of the mouth, throat, and stomach. Can cause sore throat, vomiting, diarrhea. 
Skin Contact: 
Corrosive. Symptoms of redness, pain, and severe burn can occur. 
Eye Contact: 
Corrosive. Contact can cause blurred vision, redness, pain and severe tissue burns. 
Chronic Exposure: 
Repeated exposures to calcium hypochlorite may cause bronchitis to develop with cough and/or shortness of breath. 
Aggravation of Pre-existing Conditions: 
No information found.

## 4. First Aid Measures

Inhalation: 
Remove to fresh air. If not breathing, give artificial respiration. If breathing is difficult, give oxygen. Get medical attention immediately. 
Ingestion: 
If swallowed, DO NOT INDUCE VOMITING. Give large quantities of water. Never give anything by mouth to an unconscious person. Get medical attention immediately. 
Skin Contact: 
Immediately flush skin with plenty of water for at least 15 minutes while removing contaminated clothing and shoes. Get medical attention immediately. Wash clothing before reuse. Thoroughly clean shoes before reuse. 
Eye Contact: 
Immediately flush eyes with plenty of water for at least 15 minutes, lifting lower and upper eyelids occasionally. Get medical attention immediately.

## 5. Fire Fighting Measures

Fire: 
Not combustible, but substance is a strong oxidizer and its heat of reaction with reducing agents or combustibles may cause ignition. Thermally unstable; at higher temperatures, may undergo accelerated decomposition with release of heat and oxygen. 
Explosion: 
Sealed containers may rupture when heated. An explosion can occur if either a carbon tetrachloride or a dry ammonium compound fire extinguisher is used to extinguish a fire involving calcium hypochlorite. Sensitive to mechanical impact. 
Fire Extinguishing Media: 
Use flooding quantities of water as fog or spray. Use water spray to keep fire-exposed containers cool. Avoid direct contact with water; reacts with water releasing chlorine gas. Fight fire from protected location or maximum possible distance. Do not use dry chemical fire extinguishers containing ammonium compounds. Do not use carbon tetrachloride fire extinguishers. Do not allow water runoff to enter sewers or waterways. 
Special Information: 
In the event of a fire, wear full protective clothing and NIOSH-approved self-contained breathing apparatus with full facepiece operated in the pressure demand or other positive pressure mode.

## 6. Accidental Release Measures

Remove all sources of ignition. Keep water away from spilled material. Ventilate area of leak or spill. Wear appropriate personal protective equipment.

Spills: Clean up spills in a manner that does not disperse dust into the air. Use non-sparking tools and equipment. Pick up spill for recovery or disposal and place in a closed container. Do not seal tightly.

## 7. Handling and Storage

Keep in a tightly closed container, stored in a cool, dry, ventilated area. Protect against physical damage and moisture. Isolate from any source of heat or ignition. Avoid storage on wood floors. Separate from incompatibles, combustibles, organic or other readily oxidizable materials. Containers of this material may be hazardous when empty since they retain product residues (dust, solids); observe all warnings and precautions listed for the product.

## 8. Exposure Controls/Personal Protection

Airborne Exposure Limits: 
None established. 
Ventilation System: 
A system of local and/or general exhaust is recommended to keep employee exposures as low as possible. Local exhaust ventilation is generally preferred because it can control the emissions of the contaminant at its source, preventing dispersion of it into the general work area. 
Personal Respirators: 
For conditions of use where exposure to the dust or mist is apparent, a half-face dust/mist respirator may be worn. For emergencies or instances where the exposure levels are not known, use a full-face positive-pressure, air-supplied respirator. WARNING: Air-purifying respirators do not protect workers in oxygen-deficient atmospheres. 
Skin Protection: 
Wear impervious protective clothing, including boots, gloves, lab coat, apron or coveralls, as appropriate, to prevent skin contact. 
Eye Protection: 
Use chemical safety goggles and/or a full face shield where splashing is possible. Maintain eye wash fountain and quick-drench facilities in work area.

## 9. Physical and Chemical Properties

Appearance: 
White or grayish-white powder. 
Odor: 
Chlorine-like odor. 
Solubility: 
Soluble in water; reacts, releasing chlorine gas. 
Specific Gravity: 
2.35 @ 20C 
pH: 
No information found. 
% Volatiles by volume @ 21C (70F): 
0 
Boiling Point: 
No information found. 
Melting Point: 
Decomposes above 177C (350F), releasing oxygen. 
Vapor Density (Air=1): 
6.9 
Vapor Pressure (mm Hg): 
Not applicable. 
Evaporation Rate (BuAc=1): 
No information found.

## 10. Stability and Reactivity

Stability: 
Rapidly decomposes on exposure to air. May decompose violently if exposed to heat or direct sunlight. Thermally unstable; decomposes at 177C (350F). 
Hazardous Decomposition Products: 
Calcium hypochlorite gives off oxygen, chlorine and chlorine monoxide. 
Hazardous Polymerization: 
Will not occur. 
Incompatibilities: 
Calcium hypochlorite is a strong oxidizer. Reacts with water and acids giving off chlorine gas. Forms explosive compounds with ammonia and amines. Incompatible with organic materials, nitrogen compounds and combustible materials. 
Conditions to Avoid: 
Heat, flame, moisture, dusting, sources of ignition and shock, and incompatibles.

## 11. Toxicological Information

Calcium hypochlorite: LD50 oral rat 850 mg/kg. Investigated as a tumorigen and mutagen.

--------\Cancer Lists\------------------------------------------------

---NTP Carcinogen---

Ingredient                             Known    Anticipated

------------------------------------   -----    -----------

Calcium Hypochlorite (7778-54-3)        No          No

## 12. Ecological Information

Environmental Fate: 
No information found. 
Environmental Toxicity: 
No information found.

## 13. Disposal Considerations

Whatever cannot be saved for recovery or recycling should be handled as hazardous waste and sent to a RCRA approved waste facility. Processing, use or contamination of this product may change the waste management options. State and local disposal regulations may differ from federal disposal regulations. Dispose of container and unused contents in accordance with federal, state and local requirements.

## 14. Other Information

NFPA Ratings: Health: 3 Flammability: 0 Reactivity: 1 Other: Oxidizer 
Label Hazard Warning: 
DANGER! STRONG OXIDIZER. CONTACT WITH OTHER MATERIAL MAY CAUSE FIRE. CORROSIVE. CAUSES BURNS TO ANY AREA OF CONTACT. HARMFUL IF SWALLOWED OR INHALED. WATER REACTIVE. 
Label Precautions: 
Keep from contact with clothing and other combustible materials.
Store in a tightly closed container.
Remove and wash contaminated clothing promptly.
Do not store near combustible materials.
Do not get in eyes, on skin, or on clothing.
Do not breathe dust or vapor.
Keep container closed.
Use only with adequate ventilation.
Wash thoroughly after handling.
Do not contact with water. 
Label First Aid: 
If swallowed, DO NOT INDUCE VOMITING. Give large quantities of water. Never give anything by mouth to an unconscious person. If inhaled, remove to fresh air. If not breathing, give artificial respiration. If breathing is difficult, give oxygen. In case of contact, immediately flush eyes or skin with plenty of water for at least 15 minutes while removing contaminated clothing and shoes. Wash clothing before reuse. In all cases get medical attention immediately.